


APPLICATION: WATERPROOFING - SPLIT SLAB



ASSEMBLY: FABRIC REINFORCED 215-MILS
MONOLITHIC MEMBRANE 6125®-FR

LONG FORM SPECIFICATION
PART I GENERAL

1.01
SUMMARY
A. This specification serves as a guideline and shall be adapted to suit the needs of each individual project by the architect. It is prepared in accordance with the CSI three-part section format and shall be included as a separate section under DIVISION 7 - Thermal and Moisture Protection. Improvements and other changes to the contents shall be made only with the written approval of the architect.

1.02
RELATED SECTIONS (Note to Specifier: Edit to project requirements)
A.
DIVISION 2 - Sitework [Section 02500/02870] - Paving/Site Furnishings as supplied by Sika/Hydrotech See Division 7 for specific details.
B.
DIVISION 3 - Concrete [Section 03300] - Roof Deck Surface/Substrate

The coordination of this section is necessary to facilitate the successful installation of the waterproofing membrane.

Cast in Place Concrete/Composite Deck

1.
Strength/density:
minimum  2,500 psi (17,235 kPa) compressive strength

 




minimum 115 pcf (1842 kg/m3) density

2.
Finish:


Broom finish or equivalent similar to ICRI CSP 3 to 5.  


Steel troweled finish is not desirable.

3.
Concrete Hydration (Cure):

a.
Method of Cure:  Water cure, wet coverings, paper sheets, plastic sheets or approved liquid curing compound (sodium silicate preferred). 
b.
Duration of Cure/Dry:

i.
Structural Weight Concrete:  recommend 28 days, minimum 14 days, prior to application of the membrane.

ii.
Lightweight Structural Concrete:  recommend 60 days, minimum 28 days, prior to application of membrane. Venting of the deck from the underside is recommended to facilitate drying.

iii.
The above minimum cure/dry times are recommended based upon basic concrete fundamentals and experience. Depending on conditions (i.e., ambient temperature, humidity) the concrete may be dry enough to receive application of the membrane in less than the 14 day minimum recommendation. Consult Sika/Hydrotech for specifics when less than the minimum is desired.

3. Form Release Agents: Contact Sika/Hydrotech
*REFER TO SECTION 3.02 PREPARATION, FOR ADDITIONAL SUBSTRATE TYPES*

A. Other Related Sections:

1.  Section 035000 – Cast Decks and Underlayment-Concrete roof deck surface/ substrate, and curbing. 

2. Section 05 3000 – Metal Decking- Metal roof deck surface/ substrate

3. Section 061510 – Wood Decking- Wood roof deck surface/substrate

4. Section 076000 – Flashing and Sheet Metal

5. Section 077200 – Roof Accessories- Curbs and hatches 

6. Section 079200 – Joint Sealants- Caulking and sealants

7. Section 220000 – Plumbing

8. Section 312200 – Grading- Fine grading of media

9. Section 321400 – Unit Paving – Paving 
10. Section 323300 – Site Furnishings

11. Section 328000 – Irrigation

12. Section 329300 – Plants- Turf, trees, shrubs, groundcovers, bulbs

13. Section 329400 – Planting Accessories – Metal Edging 

14. Section 330000 – Utilities

1.03
REFERENCES
A.
American Society for Testing and Materials (ASTM).

B. Canadian Government Specification Board CGSB-37.50-M89, Standard for "Asphalt, Rubberized, Hot Applied, for Roofing and Water​proofing."
C. International Concrete Repair Institute (ICRI) Concrete Surface Profile (CSP) Scale.
D. Underwriters Laboratories (UL) Class A.
1.04
SYSTEM DESCRIPTION
A.
Furnish and install a completed vertical or horizontal waterproofing assembly including surface conditioner, Hydrotech® Monolithic Membrane 6125®-FR and related flashings, protection course, Styrofoam™ brand insulation (if required), drainage course (if required), and pavers (if required). 
1.05
SUBMITTALS
A.
Certification from an approved independent testing laboratory experienced in testing this type material, that the material meets the CGSB-37.50-M89 standard for rubberized asphalt membranes, including applicable ASTM procedures. 
B. Certification that the roofing membrane has current validation by Underwriters Laboratories, or other approved independent validation service provider, of a minimum 40% recycled content (post-consumer).

C.
Certification showing full time quality control of production facilities responsible for the manufacture of the rubberized asphalt and that each batch of material is tested to ensure conformance with the manufacturers published physical properties.

D. Certification that the plant manufacturing this material has IS0 9001-2015 approval as evidenced by a copy of the official certificate.

E.
Certification showing that all roofing components are being supplied and warranted by a single-source manufacturer.

F. Certification that the extruded polystyrene insulation if used is free from CFC's.
G. Evidence that the roof membrane assembly is currently Class A listed with Underwriters

Laboratories.
H. Certification that the roof membrane assembly is currently listed as a Class 1 Roof Cover with Factory Mutual Research Corporation when required.

1.06
QUALITY ASSURANCE
A.
The Waterproofing Contractor shall demonstrate qualifications to perform the work of this Section by submitting the following documentation:

1.
Certification or license by the membrane manufacturer as a locally based, authorized applicator of the product the installer intends to use, for a minimum of five (5) years.

2.
List of at least three (3) projects, satisfactorily completed within the past five (5) years, of similar scope and complexity to this project. Previous experience submittal shall correspond to specific membrane system proposed for use by applicator.

B.
Refer to Section 1.04 SYSTEM DESCRIPTION. Include single-source for all components from the manufacturer.

C.
The rubberized asphalt membrane product shall contain an inert filler and crumb rubber to enable the product to be resistant to acids (fertilizers, building washes and acid rain) and maintain membrane thickness during application, respectively.

D.
Membrane Manufacturer shall have available an in-house technical staff to assist the contractor, when necessary, in application of the products and final inspection of the assembly.

E.
Membrane Manufacturer Qualification:  Manufacturer shall demonstrate qualifications to supply materials of this section by certifying the following:

1.
Membrane Manufacturer shall show evidence that the specified rubberized asphalt has been manufactured by the same source for forty (40) years and successfully installed on a yearly basis for a minimum of forty (40) years on projects of similar scope and complexity.

2.
Membrane Manufacturer shall not issue warranties for terms longer than they have been manufacturing their hot fluid rubberized asphalt membrane.

F.
Pre-Construction Conferences. The manufacturer will meet with the necessary parties at the jobsite to review and discuss project conditions as it relates to the integrity of the waterproofing assembly.

1.07
DELIVERY, STORAGE AND HANDLING
A.
Deliver materials in original unopened containers of packaging clearly labeled with manufacturer's name, brand name, instruction for use and all identifying numbers.

B.
Materials shall be stored in a neat, safe manner, not to exceed the allowable structural capacity of the storage area.

C. Store handle and protect products in accordance with manufacturer's instructions. Materials should be kept in a clean, dry area protected from water and direct sunlight.
D.
Store all adhesives at temperatures between 60°F (15.5°C) and 80°F (26.6°C). If exposed to lower temperatures, restore materials to 60°F (15.5°C) minimum temperature before using.

1.08
PROJECT CONDITIONS
A.
Application of the membrane shall not commence nor proceed during inclement weather. All surfaces to receive the membrane shall be free of water, dew, frost, snow, and ice.

B.
Application of membrane shall not commence nor proceed when the ambient temperature is below 0°F (-17.7°C).

C.
Preparation and application of membrane shall be conducted in well ventilated areas.

D.
Over its service life, do not expose membrane or accessories to a constant temperature in excess of 180°F (82°C) (i.e., hot pipes and vents or direct steam venting, etc.).

E.
Adhesives contain petroleum distillates and are extremely flammable.  Do not breathe vapors or use near an open fire.  Do not use in confined areas without adequate ventilation.  Consult container or packaging labels and Material Safety Data Sheets (MSDS) for specific safety information.

F.
Do not allow waste products (petroleum, grease, oil, solvents, vegetable, or mineral oil,
animal fat, etc.) to come in contact with the waterproofing membrane.  Any exposure to foreign materials or chemical discharges shall be presented to membrane manufacturer or evaluation to determine any impact on the waterproof membrane assembly performance.

G.
Concrete Deck/Wall Surface Condition.  IMPORTANT ‑ Refer to 1.02 Related Sections.
H.
Deck/Wall Preparation; refer to Section 3.02 Preparation.
I. 
The project design professional shall design the roofing/waterproofing assembly to properly locate the dew point condition and determine the need and location for a  vapor retarder to prevent excessive condensation contamination within the roofing/waterproofing assembly and/or delamination of the roofing/waterproofing membrane from the substrate. 
J.
General contractor shall assure that adequate protection is provided after installation of the membrane and accessories to prevent damage from subsequent trade traffic. 

1.09
WARRANTY
A.
Upon completion of the work, the contractor shall supply the owner with a single-source warranty of U.S. origin direct from the manufacturer.

B.
Each warranty varies in scope and terms.  CONTACT Sika/Hydrotech for exact warranty terms and conditions to meet the specific project requirements.
C.
Warranties available from the manufacturer: (Note to Specifier: Edit to project requirements)
1.
Material Warranties; excludes labor.

Duration:  2-, 5-, 10-, 15-, 20-year

2.
Watertightness Warranties; includes labor and material to maintain watertight condition.

Duration:  5-, 10-, 15-, 20-, 25-, 30-year

3.
Thermal Warranties; includes 90% retention of the original thermal value.

Duration 5-, 10-, 15-, 20, 25-, 30-year
*CONTACT Sika/HYDROTECH FOR EXACT WARRANTY TERMS AND CONDITIONS.*
PART II PRODUCTS

2.01
GENERAL
A.
Refer to Section 1.04, SYSTEM DESCRIPTION.  All components shall be obtained as a single-source from the membrane manufacturer to ensure total system compatibility and integrity.

 Manufacturer: 

Sika/Hydrotech®
100 Dan Road

Canton, Massachusetts 02021

1.888.509.3350

                 Web Site: www.hydrotechusa.com
2.02
MATERIALS
A.
Membrane

1. Membrane shall be a hot, fluid applied, rubberized asphalt membrane meeting the CGSB-37.50-M89 standard and other pertinent physical properties:

a. Hydrotech® Monolithic Membrane 6125®
	PROPERTY
	TEST METHOD
	REQUIREMENT

	Flash point
	CGSB-37.50-M89

ASTM D-92 


	> 500°F*

(260°C)

	Penetration
	CGSB-37.50-M89

ASTM D-5329


	@ 77°F (25°C) max. 98

@ 122°F (50°C) max. 187

	Flow
	CGSB-37.50-M89

ASTM D-5329
	1.0mm @ 140°F (60°C) max. 

	Toughness


	CGSB-37.50-M89


	≥ 5.5 Joules



	Ratio of Toughness to Peak Load


	CGSB-37.50-M89


	≥ 0.040



	Water Vapor Permeability
	CGSB-37.50-M89

ASTM E-96, Procedure E 


	≤ 1.7 ng/Pa.s.m2

(0.027 perm)

	Water Absorption


	CGSB-37.50-M89
	Gain in weight 0.35 g max.

Loss in weight 0.18 g max.

	Low Temperature Flexibility 

(-25°C)
	CGSB-37.50-M89


	No delamination, adhesion loss, or cracking

	Low Temperature Crack Bridging Capability


	CGSB-37.50-M89
	No cracking, adhesion loss, or splitting

	Heat Stability
	CGSB-37.50-M89
	No change in viscosity, penetra​tion, flow or low temperature flexibility

	Viscosity


	CGSB-37.50-M89


	2 - 15 seconds



	Water Resistance 

(5 days/50°C)
	CGSB-37.50-M89
	No delamination, blistering, emulsification, or deterioration

	Softening Point
	ASTM D-36
	180°F (82°C)

	Elongation
	ASTM D-5329
	1000% minimum

	Resiliency


	ASTM D-5329
	40% minimum

	Bond to Concrete

0°F (-18°C)
	ASTM D-5329


	Pass @0°F (-18°C)

	Resistance to Acid
	ASTM D-896

Procedure 7.1 (N-8)
	Pass ‑ 50% Nitric Acid

Pass ‑ 50% Sulfuric Acid



	Resistance to Hydrostatic Pressure
	ASTM D-08.22

Draft 2


	100 psi

(equals 231 foot of head water)

	Resistance to Salt Water

(20% Sodium carbonate calcium chloride)


	ASTM D-896 similar 
	No delamination, blistering, emulsification, or deterioration

	Resistance to Fertilizer

(Undiluted 15/5/5, nitrogen/phosphorus/potash)
	ASTM D-896 similar 
	No delamination, blistering, emulsification, or deterioration

	Resistance to Animal Waste


	3-year exposure


	No deterioration



	Solids Content
	
	100% - no solvents

	Recycled Content
	UL Validated
	40% (post-consumer)

(30% REACH compliant)

	Shelf Life
	
	10 years (sealed)

	Specific Gravity
	
	1.15 + .02


	* Or alternatively not less than 25oC above the manufacturer’s maximum recommended application temperature


B. Surface Conditioner (Note to Specifier: Edit to project requirements)
1.
Hydrotech® Surface Conditioner 56170

Asphaltic surface conditioner for concrete surfaces.

2.
Hydrotech® Low VOC Surface Conditioner 

LOW VOC Asphaltic surface conditioner for concrete surfaces.
3.
Hydrotech® Surface Conditioner VC 

Low VOC Compliant surface conditioner for concrete surfaces.

4.
Hydrotech® Surface Conditioner GC

Moisture Mitigating surface conditioner for concrete surfaces.

C.
Reinforcing (Note to Specifier: Edit to project requirements)
1.
Hydrotech® Flex Flash UN®

60-mil (1.5 mm) thick, uncured neoprene  flashing/(heavy duty) reinforcing sheet.

2.
Hydrotech® Flex Flash F®

Spunbonded polyester fabric (standard duty) reinforcing sheet.

3.
Hydrotech® Flex Flash FV® (vertical)

Woven fiberglass fabric reinforcing sheet (vertical applications only)

D. Flashing (Note to Specifier: Edit to project requirements)
1.
Hydrotech® Flex Flash UN®

60-mil (1.5 mm) thick, uncured neoprene  flashing/(heavy duty) reinforcing flashing sheet.

2.
Hydrotech® Flex-Flash MB®


180-mil (4 mm) thick, torch-grade, modified asphalt, reinforced flashing membrane. . Meets and exceeds requirements of ASTM D6223, Type I, Grade G.

3.       Sikalastic Rapid PMMA



Two-component, liquid applied resin membrane flashing system.

a. Sikalastic Rapid 724 (summer grade) or WW (winter grade) – poly methyl-methacrylate (PMMA) resin
b. Sikalastic Rapid 724 Detailer - poly methyl-methacrylate (PMMA resin with integral chopped polymer fiber reinforcement

c. Sikalastic Rapid Catalyst PMMA - reactive agent to initiate curing of methyl-methacrylate liquid resins and primers

d. Sikalastic Rapid Primer ASP - rapid-setting, proprietary formulation polymethyl methacrylate (PMMA) primer for asphaltic, wood, masonry, concrete, wood, and other surfaces.

e. Sikalastic Rapid Primer Metal - rapid-setting, acrylic primer for metal surfaces.

f. Sikalastic Rapid Fleece PMMA -  non-woven, needle-punched polyester fleece used as the reinforcement for Sikalastic Rapid liquid flashing details 

4.       Hydrotech® HydroSeal 1K 


           One-component, liquid applied membrane flashing system

a. Hydrotech® HydroSeal 1K PU Membrane -Aliphatic and alkaline resistant,  low VOC polyurethane (PU) resin

b. Hydrotech® HydroSeal 1K Epoxy Primer-for use on most sound substrates including concrete, masonry, plywood, metal, and bitumen-based membranes such as Monolithic Membrane 6125®

c. Hydrotech® HydroSeal 1K Fleece-heavy duty, non-woven, chopped strand polyester fabric reinforcement

d. Hydrotech® HydroSeal 1K Fiber Reinforcement-nonwoven, surface treated glass fiber reinforcement

E.
Adhesives/Sealant (Note to Specifier: Edit to project requirements)
1.
Hydrotech® Splice Tape Primer

Solvent-based, fast drying, VOC-compliant lap / seam primer

2.
Hydrotech® Splice Tape


Pressure sensitive butyl tape to bond elastomeric flashing together.

3.
Hydrotech® Low VOC Bonding Adhesive

Contact adhesive to bond elastomeric flashing to an approved substrate.

4.
SikaHyflex® - 407 EverFlash Universal


One component, non-sag, flexible, flashing sealant and weather barrier sealant designed for primer less adhesion to the most challenging substrates found in the building envelope such as, hot applied rubberized asphalt,  peel & stick window and flashing membranes

E.
Protection Course (Note to Specifier: Edit to project requirements)
1.
Hydrotech® Hydroflex® 30 (required on horizontal applications)

Fiberglass reinforced rubberized asphalt sheet.

2. Hydrotech® Thermaflo™

Extruded polystyrene, rigid, insulation, drainage board with drainage channels (vertical applications only) 
3. Styrofoam™ brand insulation as manufactured by DuPont™, marketed by  Sika Corporation Protection Board, SM, RM

Extruded polystyrene, rigid, insulation board (vertical applications only)

- 
**Certain project conditions may warrant additional protection. CONTACT Hydrotech**
F.
Prefabricated Drainage Course (if required) (Note to Specifier: Edit to project
requirements)

1. Composite drainage system: Consisting of a three-dimensional, crush-proof, HPDE, geonet drainage core and a white non-woven filter fabric meeting the following physical properties.
a.
Hydrotech® Hydrodrain®
i. 300 - filter fabric – top ply 

ii. 302 - filter fabric – top & bottom

iii. 1000 - filter fabric – top & bottom

	Compressive Strength
	ASTM D-1621
	300/302/1000 – 40,000 psf

	Thickness
	ASTM D-1777
	300/302/1000- .25 in (.64 cm)


	Flow, Q @ 3600 psf & hydraulic gradient of 1
	ASTM D-4716
	300/302/1000 – 8.5 gpm/ft width
(106.00 lpmin/m width)


	FABRIC (TOP):
	
	

	Flow
FABRIC (BOTTOM):
Flow
	ASTM D-4491
ASTM D-4491
	300/302/1000 - 150
gpm/ft2 (6105 lpmin/m2)
302/1000 - 110 gpm/ft2 (4481
lpmin/m2)



	U.V. Resistance
	ASTM D-4355
	Fully Stabilized

	Apparent Opening Size (EOS)
	CW-02215
	300/302/400/420/71000 – 70 (.212mm))

	Grab Tensile
	ASTM D-4632
	300/302/400/420/1000 - 100 lbs.
(0.445 KN)


2. Composite drainage system: Consisting of an impermeable polypropylene sheet with a high-flow dimple type drainage core with woven or nonwoven filter fabric bonded to one side.
a. Hydrotech® Hydrodrain®
i. 400 - filter fabric – top only 
ii. 420 - filter fabric top w/polyethylene sheet bonded to underside
iii. 700 - filter fabric – top
iv. 990 - filter fabric - top
	Compressive Strength
	ASTM D-1621
	400/420 - 15,000 psf
700 - 21,000 psf
990 - 33,000 psf

	Thickness
	ASTM D-1777
	400/420/700/990 - .40 in (1.016 cm)

	Flow, Q @ 3600 psf & hydraulic gradient of 1
	ASTM D-4716
	400/420 - 21 gpm/ft width
(260 lpmin/m width)
700 - 23 gpm/ft width
(286 lpmin/m width)
990 - 24 gpm/ft width
(298 lpmin/m width)

	FABRIC (TOP):
	
	

	Flow
FABRIC (BOTTOM):
Flow
	ASTM D-4491
ASTM D-4491
	400/420/700 – 150 gpm/ft2 (6105 lpmin/m2)
990 - 145 gpm/ft2 (5907 lpmin/m2)


	U.V. Resistance
	ASTM D-4355
	Fully Stabilized

	Apparent Opening Size (EOS)
	CW-02215
	400/420 – 70 (.212mm)
700/990 – 40 (.60 mm)

	Grab Tensile
	ASTM D-4632
	400/420 - 100 lbs.(0.445 KN)
700 – 360x260 lbs. (445x355 N)
990 – 365x200 lbs. (1,624x890 N)


2. Hydrotech® Thermaflo™

Extruded polystyrene, rigid, insulation, drainage board (vertical applications only)

G.
Insulation (Note to Specifier: Edit to project requirements)
Styrofoam™ Brand insulation (TYPE) as manufactured by DuPont™, marketed Sika Corporation – (Product types available:  Styrofoam™ brand, DeckMate Plus, DeckMate Plus FA, Tapered DeckMate Plus FA.) 
Extruded polystyrene rigid board insulation meeting the following physical properties. 

a.
Insulation shall meet ASTM C-578, Type VI, V or VII.

b.
Minimum compressive strength, ASTM D-1621, 40, 60 or 100psi (276 or 414 or 689 kPa) (variance by type of product).

c.
Maximum water absorption by volume per ASTM C-272, 0.1%.

d.
Water vapor permeance for 1" product per ASTM E-96, 0.8 perm (max.) 

e.
Insulation shall have an R value of 5.0 F ft2 h/Btu/in. (0.88 K m2/W) of thickness when tested at 75°F (23.9°C) mean temperature in accordance with ASTM C-518.

f.
Product shall be free of CFC's.
         2.
Geofoam Lightweight Fill as manufactured by Atlas, marketed by  Sika/Hydrotech  



Expanded polystyrene geofoam insulation for use as structural fill. 

a. Geofoam Lightweight Fill using 100 percent virgin feedstock as manufactured by Atlas Molded Products and marketed by Sila/Hydrotech 

b. Geofoam shall meet ASTM D6817. 
c. Surface Burning: Class A, with Flame Spread Index (FSI) of <25, and Smoke Developed Index (SDI) of <450, in compliance with ASTM E84 or UL723.
(Note to Specifier: CONSULT Sika/Hydrotech for recommended product type.)

H.    Air Layer (Note to Specifier: Edit to project requirements – air layer may be  required  for thermal warranty - CONSULT Sika/Hydrotech) 
1. Hydrotech® Hydrodrain® AL - to be used as the air space between the surface of  DuPont Styrofoam™ insulation boards and a monolithic pour of concrete or when pavers are to be placed directly on the insulation 

I.
Filter Fabric (if required)

1.
Hydrotech® Stone Filter Fabric

Water permeable polymeric fabric.

J.
Topping Materials (Note to Specifier: Edit to project requirements)
1.
Concrete Pour Topping

(Note to specifier: DuPont™, manufacturers of Styrofoam™ 
brand insulation, recommends the incorporation of an air layer   between the insulation and concrete. Sika Corporation suggests the use of Hydrodrain® AL for this purpose.)
2.
Asphalt Paving Overlay

(Note to specifier: When asphalt paving will be placed directly over the waterproofing, CONTACT Sika Corporation for suggestions and recommenda​tions.)

PART III EXECUTION


3.01
INSPECTION
A.
The waterproofing contractor shall examine all surfaces to receive the waterproofing assembly to verify it is acceptable and proper for the application of the membrane.  Refer to Sika Corporation’s Pre-Installation & Application Guidelines.
B.
The waterproofing contractor shall not proceed with the installation of the waterproofing membrane assembly until all deck defects have been corrected.

3.02
PREPARATION
A. All surfaces shall be dry, smooth, free of depressions, voids, protrusions, clean and free of unapproved curing compounds, form release agents, and other surface contaminants.

(Note to Specifier: Edit to project requirements)


1.
Cast in-place concrete (slab or wall)/Composite deck

a.
Poured in place concrete shall be monolithic, smooth, free of voids, spalled areas, laitance, honeycombs, and sharp protrusions.


b.
Refer to Section 1.02 of this specification, Division 3.

2.
Precast concrete decks

a.
Precast units shall be mechanically secured to minimize differential movement and all joints between units shall be grouted or caulked.

b.
Joints shall be pre-detailed with membrane and the appropriate manufacturer required reinforcing prior to full membrane application. 

3.
Retrofit/Tear-Off Application
a.
Asphalt, coal tar pitch, or other existing membrane shall be removed. CONTACT Sika/Hydrotech.

b.
Deck type acceptable to Hydrotech.
B.
Substrate cleaning

1.
Thoroughly sweep the substrate which is to receive the waterproofing membrane.

1. Substrate shall also be blown clean using an air compressor to remove any remaining loose debris.

2. Final check to determine if concrete has been properly cleaned is to apply a test patch of Monolithic Membrane 6125® to the surface and check its adhesion.

3.03
INSTALLATION
Surface conditioner application (to concrete substrates only)
1.
Hydrotech® Surface Conditioner 56170 

a. Apply the surface conditioner to the concrete using a handheld sprayer evenly at a rate of 300 to 600 SF/gallon (7.4 - 14.7 m2/L) depending on surface texture. Surface conditioner shall "tan" the surface, not blacken it.

b. Allow sufficient time for the surface conditioner to thoroughly dry prior to the membrane application.

2.
Hydrotech® Low VOC Surface Conditioner 

a. Apply the surface conditioner to the concrete using a handheld sprayer evenly at a rate of 300 to 600 SF/gallon (7.4 - 14.7 m2/L) depending on surface texture. Surface conditioner shall "tan" the surface, not blacken it.

b. Allow sufficient time for the surface conditioner to thoroughly dry prior to the membrane application.

c. Do not store below 40°F (4°C) or above 110°F (43°C).

3.
Hydrotech® Surface Conditioner VC  

a. Thoroughly mix contents

b. Cannot be applied at temperatures below 40°F (4°C)

c. Apply the surface conditioner to the concrete using a handheld sprayer evenly at a rate of 300 to 600 SF/gallon (7.4 - 14.7 m2/L) depending on surface texture. Surface conditioner shall "tan" the surface, not blacken it.

d. Allow sufficient time for the surface conditioner to thoroughly dry prior to the membrane application.

e. Do not store below 40°F (4°C) or above 110°F (43°C).

4.
Hydrotech® Surface Conditioner GC 

a. Apply the surface conditioner GC in two coats, to the concrete using a nap roller evenly, no puddling, at a rate of 200-250 square feet (both coats) depending on surface texture. Surface conditioner shall be “milky white" when applied and will dry clear. 

b. Ambient and concrete surface temperatures must be at least 40° F (4° C) 

c. Optimum installation temperatures are between 45° F and 100° F (37° C)

d. Allow sufficient time for the surface conditioner to thoroughly dry prior to the membrane application.

e. Do not store below 65°F (4°C) or above 90°F (43°C).

B.
Membrane preparation

1. The membrane shall be heated in double jacketed, oil bath or hot air melter with mechanical agitation, specifically designed for the preparation of a rubberized asphalt membrane.

2. Heat membrane until membrane can be drawn-free flowing at a temperature range between 350°F (176°C) and 375°F (190°C).

C.
Detailing/Flashing

1.
All detailing and flashing shall be done in accordance with the manufacturer's standard guideline details.

2.
All detailing and flashing shall be completed before installing the membrane over the field of the substrate.

3. All liquid-applied, resin flashings shall be applied over properly completed membrane flashing details in accordance with the manufacturer’s standard guideline details. 

D.
Membrane Application

1. Apply the rubberized asphalt membrane at a rate to provide a continuous, monolithic coat of 90 mil minimum (approximately 2.3 mm), into which is fully embedded a layer of the spunbonded polyester fabric reinforcing sheet, followed by another continuous monolithic coat of membrane at an average thickness of 125 mil (approx. 3.2 mm).  Total membrane thickness shall be 215 mils average (approx. 5.5 mm), 180 mils minimum.(Note to Specifier: For vertical foundation wall applications, woven fiberglass reinforcing may be used in lieu of spunbonded polyester.)

2. Overlap fabric reinforcing sheet 2-3 inches (50.8 mm – 76.2 mm) with membrane between sheets. 

3.04
SEPARATION/PROTECTION LAYER INSTALLATION
A. Protection layer shall be installed as follows: (Note to Specifier: Edit to project requirements)
1.
Embed the protection sheet/rigid insulation board into the membrane while it is still warm to insure a good bond.

2.
Overlap adjoining sheet edges a minimum of 2"-3" (50.8 mm - 76.2 mm) to insure complete coverage. Rigid insulation board materials shall not be overlapped.

3.
The completed membrane/protection assembly shall be covered with subsequent topping materials as soon as possible, within 30 days of membrane installation.

3.05
MEMBRANE INTEGRITY TEST
A. The roof area or portions thereof shall be leak tested by means of Electronic Leak Detection (ELD) or by ponding water at a minimum depth of 2" (50.8 mm) for a period of 48 hours to check the integrity of the membrane installation.

1. ELD testing should be performed on all installed membrane assembly. Testing is to be performed in accordance with ASTM D7877 or ASTM D8231. Areas that are ELD tested should be covered immediately

2. VERIFY that the structure can support the deadload weight of a water test before testing.

3. If leaks should occur the water shall be drained completely and the membrane installation repaired.

B. In the event of excessive damage to the membrane assembly, Electronic Leak Detection testing shall be required prior to the placement of subsequent overburden. 

3.06
DRAINAGE COURSE / INSULATION / FILTER FABRIC / PAVER PLACEMENT
A.
General

1.
Contractor shall examine the deck area to be covered with subsequent topping materials in order to insure that all deck areas have received the membrane, the membrane is free of damage, it is properly protected, and all flashing has been properly installed, before placing the insulation.

2.
The drainage course (if required), insulation (if required), and other subsequent topping materials shall be installed as each section is completed.

B.
Prefabricated Drainage Course Placement (if required)

1.
Install the drainage course on horizontal and vertical surfaces in accordance with the manufacturer's recommendations.

2.
Layout and position drainage course and allow to lay flat. Cut and fit drainage course to perimeter and penetrations.

3. The geotextile overlapped edges may be bonded to the adjacent drainage course geotextile with an appropriate adhesive to ensure continuous geotextile integrity.
4.
Drainage course shall be covered with subsequent overburden within 10 – 14 days of installation.
(Note to specifier: If drainage layer is being installed as an AIR LAYER, placement of the drainage course follows installation of insulation (if required). CONTACT Sika Corporation.) 
C.
Insulation Placement (if required)

1. Loose lay (horizontal applications) in a staggered manner and tightly butt together all insulation boards. The maximum acceptable opening between insulation boards is 3/8" (9.5 mm). Insulation shall be installed within 3/4" (19 mm) of all projections, penetrations, etc.

2. When multi-layer insulation applications are involved the bottom layer of insulation shall be the thickest layer and shall be a minimum of 2" thick (50.8 mm). All layers shall be installed unadhered to each other and all joints staggered in relation to underlying layers.

3. For vertical, multi-layer applications, the second layer of insulation board shall be spot adhered to the protection layer with appropriate adhesive or additional rubberized asphalt membrane. 

3.07
JOB COMPLETION
A. The contractor and a representative of the membrane manufacturer shall inspect the waterproofing assembly and notify the contractor of any defects. All defects shall be corrected.

B. Clean up all debris and equipment.


END OF SECTION

The preceding specifications are provided by Sika Corporation as a guide for informational purposes only and are not intended to replace sound engineering practice and judgment and shall not be relied upon for that purpose. Sika Corporation makes no warranty of any kind, either express or implied, as to the accuracy, completeness or the contents of these guide specifications. Sika Corporation assumes no liability with respect to the provision or use of these guide specifications, nor shall any legal relationship be created by, or arise from, the provision of such specifications  SIKA SHALL NOT BE RESPONSIBLE UNDER ANY LEGAL THEORY TO ANY THIRD PARTY FOR ANY DIRECT OR CONSEQUENTIAL DAMAGES OF ANY KIND ARISING FROM THE USE OF THESE GUIDE SPECIFICATIONS.  The specifier, architect, engineer or design professional or contractor for a particular project bears the sole responsibility for the preparation and approval of the specifications and determining their suitability for a particular project or application.

Prior to each use of any Sika product, the user shall always read and follow the warnings and instructions on the product's most current Technical Data Sheet, product label and Material Safety Data Sheet which are available at www.usa.sika.com/roofing or www.hydrotechusa.com or by calling (800) 933-7452.  Nothing contained in any Sika materials relieves the user of the obligation to read and follow the warnings and instructions for each Sika product as set forth in the current Technical Data Sheet, product label, and Material Safety Data Sheet prior to product use.

05.23
13
copyright

